## Slide 1
Notes: COVER SLIDE
If you have a very long title, make it upper and lower case instead of all caps.

## Slide 2: // Agenda
1 | Project Elements and Objectives
2 | Study Area and Wastewater Flows
3 | Hydraulic Model Development
4 | Condition Assessment
5 | Proposed Improvements and Capital Improvement Plan

## Slide 3: Project Elements and Objectives
Notes: DIVIDER SLIDE – SECOND LEVEL
The yellow text may not be appropriate on every divider slide. If it doesn’t work with your message, delete the yellow text.

## Slide 4: // The objective of the master plan is to develop a prioritized capital improvement plan for the collection system’s needs through 2045
Flow Monitoring
Deficiencies and Projects
Capital Improvement Program
Hydraulic Analysis and Condition Assessment

## Slide 5: Study Area
Notes: DIVIDER SLIDE – SECOND LEVEL
The yellow text may not be appropriate on every divider slide. If it doesn’t work with your message, delete the yellow text.

## Slide 6: // The City provided planning data that was used to develop future flow projections
Housing Element
Planned Developments
Accessory Dwelling Units
General Plan Land Use

## Slide 7: // The City’s service area is largely built out

## Slide 8: // Known developments could add about 1,300 additional homes

## Slide 9: // The Regional Housing Needs Assessment identifies the need for 4,436 additional homes beyond the 1,299 homes identified as known development

## Slide 10: // The potential addition of 1,150 accessory dwelling units (ADUs) were also included in the analysis

## Slide 11: // The City’s average dry weather flow is projected to increase from 5.6 million gallons per day (mgd) to 6.5 mgd by 2045
Flow Component | Average Dry Weather Flow (mgd)
Existing Wastewater Flow | 5.56
Future Flow Contribution(1) | 
RHNA Required Units (5,700 units) | 0.86
Planned Developments(2) | 0.09
ADU’s(3) | 0.02
Future Growth Subtotal | 0.97
Total Estimated Future Flow | 6.53
Notes:
Based on 55 gpd/person and 2.74 people per EDU (151 gpd/edu).
Includes planned developments from City’s website expected to contribute to an increase in wastewater flows.
Assumes 8 ADU’s per year for 20 years, at 151 gpd/ADU.

## Slide 12: Hydraulic Model Development
Notes: DIVIDER SLIDE – SECOND LEVEL
The yellow text may not be appropriate on every divider slide. If it doesn’t work with your message, delete the yellow text.

## Slide 13: // A temporary flow monitoring program was conducted to quantify wastewater flows within the City’s service area
Legend:
Flowmeter
Flow Direction
XX
Flow Split/Diversion

## Slide 14: // The flow monitoring program showed a substantial inflow response into the sewer system during wet weather conditions
Chart: Flow (mgd)
 | 6.251

## Slide 15: // Smoke testing is recommended to help identify and eliminate inflow sources in the system

## Slide 16: // A hydraulic model of the system was developed in the InfoWorks platform developed by Innovyze

## Slide 17: // The hydraulic model was calibrated to both dry and wet weather flow conditions
Site FM-12
Site FM-12

## Slide 18: Condition Assessment
Notes: DIVIDER SLIDE – SECOND LEVEL
The yellow text may not be appropriate on every divider slide. If it doesn’t work with your message, delete the yellow text.

## Slide 19: // A visual condition assessment was performed for the City’s existing lift station

## Slide 20: // Closed Circuit Television (CCTV) inspections were performed for 8-miles of sewer mains (80 miles had previously been inspected by the City)

## Slide 21: // Level 1 inspections were performed for every manhole within the City’s collection system

## Slide 22: // Analysis of the condition assessment results showed that additional investment in pipeline rehabilitation is necessary to avoid pipeline failures in the future
~ 8-percent of the City’s gravity mains are targeted for rehabilitation in the next 10-years

## Slide 23: Proposed Improvements and Capital Improvement Plan
Notes: DIVIDER SLIDE – SECOND LEVEL
The yellow text may not be appropriate on every divider slide. If it doesn’t work with your message, delete the yellow text.

## Slide 24: // Existing and future system capacity upgrades were developed using the hydraulic model

## Slide 25: // A prioritized CIP was developed to fund collection system upgrades and rehabilitation through 2045
Project Type | 10-Year Capital Improvement Cost ($) | 2033 and Beyond Capital Improvement Cost ($) | Total Capital Improvement Cost ($)
Capacity Upgrades | $0.0M | $14.4M | $14.4M
Rehabilitation | $8.7M | $49.7M | $58.4M
Other | $1.6M | $0.0M | $1.6M
Total | $10.3M | $64.1M | $74.4M

## Slide 26
Questions?